## Information
Name | Units | Description
VTEM | V | Voltage supplied to the TEMs
T amb | ºC | Ambient temperature
HR amb | % | Ambient reltive humidity
T glyc in | ºC | Water/glycol mixture inlet temperature
T glyc out | ºC | Water/glycol mixture outlet temperature
T suc | ºC | Compressor inlet temperature
T dis | ºC | Compressor outlet temperature
T gc in | ºC | Gas-cooler inlet temperature
T gc out | ºC | Gas-cooler outlet temperature
T bp in | ºC | Back-pressure inlet temperature
T exp in | ºC | Expansion inlet temperature
T ev out | ºC | Evaporator outlet temperature
T TESC 1 in | ºC | Temperature at the inlet of the TESC
T TESC 12 | ºC | Temperature at the inlet of block 2 of the TESC
T TESC 23 | ºC | Temperature at the inlet of block 3 of the TESC
T TESC 34 | ºC | Temperature at the inlet of block 4 of the TESC
T TESC 4 out | ºC | Temperature at the outlet of the TESC
T TEM C1 | ºC | TEM cold side temperature at block1
T TEM H1 | ºC | TEM hot side temperature at block 1
T TEM C2 | ºC | TEM cold side temperature at block 2
T TEM H2 | ºC | TEM hot side temperature at block 2
T TEM C3 | ºC | TEM cold side temperature at block 3
T TEM H3 | ºC | TEM hot side temperature at block 3
T TEM C4 | ºC | TEM cold side temperature at block 4
T TEM H4 | ºC | TEM hot side temperature at block 4
Psuc | bar | Compressor inlet pressure
Pdis | bar | Compressor outlet pressure
Pgc out | bar | Gas-cooler outlet pressure
P exp | bar | Expansion pressure
P tank | bar | Tank pressure
Pev in | bar | Evaporator inlet pressure
Pev out | bar | Evaporator outlet pressure
TESC DP | mbar | Difference of pressure at the TESC
Compressor Power | W | Power consumed by the compressor
M ref | kg/h | CO2 mass flow
M glyc | kg/h | Water/glycol mixture mass flow
TEM Power | W | Power consumed by the TEMs
Fan Power | W | Power consumed by the fans

## Vfan=12 V
VTEM | T amb | HR amb | T glyc in | T glyc out | T suc | T dis | T gc in | T gc out | T bp in | T exp in | T ev out | T TESC 1 in | T TESC 12 | T TESC 23 | T TESC 34 | T TESC 4 out | T TEM C1 | T TEM H1 | T TEM C2 | T TEM H2 | T TEM C3 | T TEM H3 | T TEM C4 | T TEM H4 | Psuc | Pdis | Pgc out | P exp | P tank | Pev in | Pev out | TESC DP | Compressor Power | M ref | M glyc | TEM Power | Fan Power
V | ºC | % | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | bar | bar | bar | bar | bar | bar | bar | mbar | W | kg/h | kg/h | W | W
0.5 | 30.1219 | 54.563 | -4.7178 | -7.9393 | 5.3271 | 80.9681 | 67.9676 | 33.0748 | 31.0505 | 27.9193 | -6.1001 | 33.2972 | 32.3741 | 31.9739 | 31.3176 | 31.1629 | 32.5493 | 33.0951 | 31.4153 | 32.6059 | 31.1249 | 33.0034 | 30.7881 | 32.9828 | 26.666 | 83.3134 | 83.2149 | 83.1162 | 67.6871 | 26.7004 | 26.4944 | 98.2656 | 269.6688 | 7.1933 | 99.2812 | 1.11 | 12.48
1 | 30.1031 | 54.7839 | -4.6387 | -8.0738 | 5.3894 | 80.9828 | 67.9122 | 32.8895 | 29.4774 | 26.7826 | -6.3405 | 33.0912 | 31.8928 | 31.2059 | 30.0964 | 29.574 | 31.9223 | 33.9784 | 30.3827 | 33.351 | 29.786 | 33.7228 | 29.1264 | 33.6878 | 26.4093 | 83.3625 | 83.2315 | 83.1469 | 66.0201 | 26.4421 | 26.2366 | 96.1719 | 269.2135 | 6.9767 | 99.1448 | 3.87 | 12.48
1.5 | 30.1263 | 54.8875 | -4.4509 | -7.9905 | 4.8308 | 80.8205 | 67.9361 | 33.059 | 28.2728 | 25.6976 | -6.2117 | 33.2581 | 31.5755 | 30.551 | 29.0341 | 28.2537 | 31.574 | 34.8444 | 29.5782 | 34.1092 | 28.5998 | 34.4205 | 27.458 | 34.1651 | 26.4931 | 83.231 | 83.0935 | 83.0081 | 64.4385 | 26.5097 | 26.3142 | 99.8281 | 270.4276 | 6.8612 | 99.4667 | 8.2 | 12.48
2 | 30.0852 | 54.6563 | -4.4074 | -7.8973 | 4.9876 | 80.9148 | 67.8796 | 32.9166 | 26.9155 | 24.6001 | -6.166 | 33.0648 | 31.134 | 29.6321 | 27.6553 | 26.6402 | 31.2498 | 35.7612 | 28.5187 | 34.7871 | 27.2611 | 34.9952 | 25.8663 | 34.7964 | 26.6589 | 83.3384 | 83.244 | 83.1777 | 62.6084 | 26.6802 | 26.4785 | 91.2812 | 270.8828 | 6.9417 | 99.8625 | 13.66 | 12.48
2.5 | 30.0068 | 54.5271 | -4.2981 | -8.0123 | 4.9057 | 80.9227 | 67.9367 | 32.8222 | 25.6114 | 23.7288 | -6.2027 | 33.0135 | 30.6609 | 28.8529 | 26.6145 | 25.2717 | 30.8443 | 36.733 | 27.6386 | 35.4504 | 26.0253 | 35.796 | 24.3375 | 35.4613 | 26.4922 | 83.1994 | 83.0644 | 82.9292 | 61.3643 | 26.5138 | 26.3117 | 134.4219 | 270.124 | 7.269 | 99.0906 | 21.05 | 12.48
3 | 30.0656 | 54.626 | -4.1524 | -8.0518 | 4.5545 | 80.6958 | 67.8349 | 32.8772 | 24.381 | 22.8682 | -6.1716 | 33.0879 | 30.4293 | 28.1595 | 25.6443 | 23.9913 | 30.3804 | 37.6468 | 26.8379 | 36.4239 | 24.8791 | 36.5087 | 22.8342 | 36.1968 | 26.4486 | 83.5131 | 83.3687 | 83.2317 | 60.0139 | 26.4699 | 26.2703 | 98.1667 | 269.3653 | 6.4417 | 99.974 | 29.33 | 12.48
3.5 | 30.2339 | 54.3932 | -4.1122 | -8.0386 | 4.6695 | 80.8307 | 67.9435 | 33.2162 | 23.5136 | 22.0874 | -6.2141 | 33.277 | 30.1692 | 27.6979 | 24.8576 | 22.8887 | 30.0919 | 38.7365 | 26.0853 | 37.4371 | 23.9235 | 37.4717 | 21.5632 | 37.0603 | 26.4361 | 83.5539 | 83.4369 | 83.3772 | 58.9952 | 26.4555 | 26.2534 | 96.401 | 270.124 | 6.4125 | 99.7938 | 38.76 | 12.48
4 | 30.1219 | 54.5094 | -3.9326 | -7.7121 | 4.5682 | 80.8111 | 67.9312 | 33.0814 | 22.3211 | 21.219 | -6.0374 | 33.2639 | 29.7604 | 26.7942 | 23.6362 | 21.3758 | 29.6577 | 39.522 | 25.1135 | 38.1227 | 22.6302 | 38.0272 | 19.9688 | 37.7022 | 26.6526 | 83.4798 | 83.3255 | 83.1203 | 57.5927 | 26.6771 | 26.4723 | 132.2448 | 270.7311 | 6.9413 | 100.5823 | 51.93 | 12.48
6 | 30.1219 | 54.3063 | -3.7283 | -7.7288 | 2.876 | 80.3338 | 67.7054 | 33.1722 | 18.4797 | 18.4034 | -6.1166 | 33.0964 | 28.6125 | 24.5543 | 20.2405 | 17.2748 | 28.5297 | 43.858 | 22.4349 | 42.0184 | 18.7912 | 41.6849 | 15.226 | 41.2466 | 26.647 | 83.2252 | 83.1533 | 82.9009 | 53.8285 | 26.6702 | 26.4654 | 121.1094 | 270.5793 | 6.7319 | 101.0063 | 111.23 | 12.48
8 | 30.1221 | 54.5641 | -3.6077 | -7.7898 | 1.9468 | 80.2222 | 67.6633 | 33.1252 | 15.7241 | 16.4492 | -6.1029 | 33.0574 | 27.5859 | 22.6413 | 17.5051 | 13.9083 | 27.6502 | 48.9174 | 20.273 | 46.5523 | 15.804 | 46.2139 | 11.4639 | 45.7377 | 26.6174 | 83.375 | 83.2531 | 83.1395 | 51.2693 | 26.6303 | 26.4265 | 105.7604 | 272.7039 | 6.9813 | 101.1125 | 204.26 | 12.48
10 | 30.1172 | 54.4135 | -3.6716 | -7.8413 | 2.0429 | 80.1476 | 67.6712 | 33.0837 | 14.1878 | 15.2822 | -6.1159 | 32.8803 | 26.8049 | 21.3229 | 15.8242 | 12.0421 | 26.6582 | 53.894 | 18.5664 | 51.4457 | 13.7461 | 50.9537 | 9.0941 | 50.618 | 26.6215 | 83.4208 | 83.3155 | 83.2508 | 49.782 | 26.635 | 26.4337 | 93.0052 | 271.0346 | 7.1577 | 101.15 | 314.63 | 12.48

## Vfan=9 V
VTEM | T amb | HR amb | T glyc in | T glyc out | T suc | T dis | T gc in | T gc out | T bp in | T exp in | T ev out | T TESC 1 in | T TESC 12 | T TESC 23 | T TESC 34 | T TESC 4 out | T TEM C1 | T TEM H1 | T TEM C2 | T TEM H2 | T TEM C3 | T TEM H3 | T TEM C4 | T TEM H4 | Psuc | Pdis | Pgc out | P exp | P tank | Pev in | Pev out | TESC DP | Compressor Power | M ref | M glyc | TEM Power | Fan Power
V | ºC | % | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | bar | bar | bar | bar | bar | bar | bar | mbar | W | kg/h | kg/h | W | W
0.5 | 30.0471 | 54.9437 | -4.8347 | -8.1349 | 5.4829 | 81.1823 | 68.0106 | 32.8132 | 30.8796 | 27.8152 | -6.4242 | 33.0757 | 32.3233 | 31.9466 | 31.3006 | 31.1685 | 32.3656 | 33.5086 | 31.3969 | 32.7341 | 31.0661 | 32.9962 | 30.7289 | 33.087 | 26.4171 | 83.2218 | 83.0868 | 83.0214 | 67.8283 | 26.4443 | 26.2382 | 97.8073 | 271.0346 | 7.0692 | 98.2854 | 1.03 | 5.84
1 | 30.0352 | 54.7589 | -4.6851 | -8.0317 | 5.2847 | 81.1588 | 68.0082 | 32.7492 | 29.7101 | 26.8974 | -6.3363 | 33.0046 | 31.8882 | 31.2283 | 30.22 | 29.8154 | 32.0381 | 34.5395 | 30.5516 | 33.5704 | 29.9605 | 33.8865 | 29.3044 | 33.785 | 26.4903 | 83.2368 | 83.0968 | 83.0347 | 66.2222 | 26.5244 | 26.3154 | 102.8333 | 271.6416 | 7.19 | 99.049 | 3.72 | 5.84
1.5 | 30.1122 | 54.8458 | -4.4174 | -8.0577 | 5.0427 | 81.0307 | 67.9976 | 33.0045 | 28.5674 | 25.9597 | -6.2417 | 33.1447 | 31.5865 | 30.6091 | 29.2014 | 28.512 | 31.6509 | 35.7739 | 29.5715 | 34.5553 | 28.8451 | 34.6781 | 27.8348 | 34.5832 | 26.5034 | 83.2377 | 83.1218 | 83.0771 | 64.7181 | 26.535 | 26.3269 | 96.6094 | 271.4898 | 7.0094 | 98.9958 | 7.78 | 5.84
2 | 30.0224 | 54.7854 | -4.3071 | -8.0775 | 5.2551 | 80.9816 | 67.9034 | 32.788 | 27.1648 | 24.9566 | -6.2542 | 32.956 | 31.1102 | 29.7772 | 28.1264 | 27.0998 | 31.1564 | 36.6538 | 28.6851 | 35.3171 | 27.5116 | 35.439 | 26.2092 | 35.26 | 26.443 | 83.2801 | 83.1218 | 83.0838 | 63.2521 | 26.4723 | 26.269 | 109.5781 | 270.8828 | 6.9737 | 99.0229 | 13.4 | 5.84
2.5 | 30.0677 | 54.7781 | -4.301 | -8.0397 | 5.0568 | 80.9715 | 67.925 | 32.9019 | 26.1015 | 24.0803 | -6.2056 | 33.0458 | 30.889 | 29.1935 | 27.093 | 25.7966 | 30.8681 | 37.81 | 27.9463 | 36.2493 | 26.4872 | 36.2504 | 24.9564 | 36.177 | 26.5224 | 83.1361 | 82.9879 | 82.8801 | 61.9679 | 26.5425 | 26.3434 | 125.625 | 269.9723 | 7.251 | 99.7625 | 20.6 | 5.84
3 | 30.0102 | 54.8677 | -4.1924 | -7.9791 | 4.8319 | 80.8419 | 67.8836 | 32.7986 | 24.8738 | 23.1187 | -6.153 | 32.9762 | 30.5136 | 28.4679 | 25.9044 | 24.3922 | 30.5016 | 39.0852 | 26.957 | 37.2179 | 25.2288 | 37.2001 | 23.3145 | 36.892 | 26.5022 | 83.1711 | 83.0519 | 82.9408 | 60.4644 | 26.5322 | 26.3229 | 112.1458 | 270.124 | 7.3898 | 99.9 | 29.31 | 5.84
3.5 | 30.0195 | 54.9474 | -4.1988 | -8.003 | 4.757 | 80.802 | 67.8456 | 32.8185 | 23.8974 | 22.4105 | -6.2606 | 32.9786 | 30.1152 | 27.7761 | 25.1081 | 23.3316 | 30.2055 | 40.4463 | 26.2884 | 38.4224 | 24.3159 | 38.283 | 22.1445 | 37.965 | 26.4651 | 83.3475 | 83.1966 | 83.0813 | 59.4087 | 26.4942 | 26.2868 | 104.849 | 270.124 | 6.9494 | 99.9573 | 39.38 | 5.84
4 | 30.0437 | 55.0057 | -3.9126 | -7.852 | 4.183 | 80.698 | 67.8279 | 32.9985 | 22.9861 | 21.6066 | -6.1124 | 33.2568 | 29.9877 | 27.3559 | 24.2756 | 22.2478 | 30.0231 | 41.9147 | 25.6124 | 39.6833 | 23.3434 | 39.4054 | 20.9312 | 39.0158 | 26.5486 | 83.5098 | 83.3886 | 83.3572 | 58.275 | 26.5699 | 26.3664 | 90.4635 | 271.0346 | 6.604 | 100.3 | 50.97 | 5.84

## Vfan=6 V
VTEM | T amb | HR amb | T glyc in | T glyc out | T suc | T dis | T gc in | T gc out | T bp in | T exp in | T ev out | T TESC 1 in | T TESC 12 | T TESC 23 | T TESC 34 | T TESC 4 out | T TEM C1 | T TEM H1 | T TEM C2 | T TEM H2 | T TEM C3 | T TEM H3 | T TEM C4 | T TEM H4 | Psuc | Pdis | Pgc out | P exp | P tank | Pev in | Pev out | TESC DP | Compressor Power | M ref | M glyc | TEM Power | Fan Power
V | ºC | % | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | ºC | bar | bar | bar | bar | bar | bar | bar | mbar | W | kg/h | kg/h | W | W
0.5 | 30.0435 | 55.0714 | -4.7473 | -7.9671 | 5.4691 | 81.3166 | 68.1004 | 32.8075 | 31.1683 | 27.98 | -6.1644 | 33.1823 | 32.4782 | 32.1184 | 31.4619 | 31.418 | 32.5171 | 33.996 | 31.5047 | 33.1417 | 31.2252 | 33.1962 | 31.0049 | 33.4404 | 26.6261 | 83.2501 | 83.1109 | 83.0489 | 67.9345 | 26.6534 | 26.4511 | 96.6979 | 271.4898 | 6.9542 | 99.5281 | 0.98 | 2.81
1 | 29.993 | 55.0828 | -4.7003 | -8.0688 | 5.4805 | 81.3952 | 68.1695 | 32.7519 | 30.0476 | 27.1551 | -6.3242 | 32.9946 | 31.9963 | 31.4914 | 30.5504 | 30.2609 | 32.0054 | 35.1202 | 30.7561 | 34.1355 | 30.2141 | 34.1599 | 29.7613 | 34.337 | 26.4218 | 83.261 | 83.15 | 83.0838 | 66.731 | 26.4524 | 26.2494 | 96.9219 | 271.6416 | 6.9419 | 98.7635 | 3.5 | 2.81
1.5 | 30.0659 | 55.0156 | -4.398 | -7.9637 | 4.894 | 81.3991 | 68.3026 | 32.9043 | 28.9295 | 26.3169 | -6.0878 | 33.1803 | 31.7131 | 30.8607 | 29.6301 | 29.0257 | 31.7693 | 36.7745 | 30.0101 | 35.5531 | 29.1955 | 35.5128 | 28.4154 | 35.5301 | 26.595 | 83.2759 | 83.1392 | 83.0563 | 65.3045 | 26.6182 | 26.4197 | 105.8073 | 271.0346 | 7.0435 | 99.8823 | 7.62 | 2.81
2 | 30.0281 | 55.3531 | -4.3449 | -7.9654 | 4.9355 | 81.3303 | 68.2342 | 32.8516 | 28.067 | 25.5146 | -6.1787 | 33.1513 | 31.5124 | 30.4033 | 28.8433 | 27.9759 | 31.501 | 38.3737 | 29.3038 | 36.8831 | 28.3513 | 36.8228 | 27.2127 | 36.7257 | 26.5545 | 83.2193 | 83.0552 | 83.0281 | 64.0536 | 26.5795 | 26.3801 | 110.6927 | 271.3381 | 6.7556 | 100.1865 | 13.2 | 2.81
2.5 | 30.0125 | 55.2146 | -4.3437 | -7.9296 | 5.0077 | 81.3197 | 68.222 | 32.7795 | 26.975 | 24.8071 | -6.0727 | 33.1096 | 31.0511 | 29.6487 | 27.8891 | 26.8687 | 31.1965 | 39.7026 | 28.584 | 37.9848 | 27.3214 | 37.9107 | 25.9919 | 37.7247 | 26.6221 | 83.2668 | 83.1883 | 83.0505 | 62.8704 | 26.6453 | 26.4402 | 115.0156 | 272.0968 | 6.8498 | 100.3385 | 20.09 | 2.81
3 | 30.0518 | 54.7849 | -4.117 | -7.8689 | 4.4906 | 81.2119 | 68.2298 | 32.911 | 25.8219 | 23.9195 | -5.9541 | 33.0351 | 30.7575 | 29.0345 | 26.8694 | 25.5311 | 30.8435 | 41.1463 | 27.8572 | 39.2588 | 26.2779 | 39.1766 | 24.6071 | 38.8529 | 26.6261 | 83.1037 | 83.0195 | 82.9366 | 61.6038 | 26.6543 | 26.4449 | 115.3229 | 271.9451 | 7.3412 | 99.9927 | 28.7 | 2.81
3.5 | 30.0023 | 54.9443 | -4.2498 | -7.8913 | 4.9459 | 81.2094 | 68.1587 | 32.7458 | 24.9251 | 23.1873 | -6.1851 | 33.0452 | 30.4999 | 28.4744 | 26.0799 | 24.5025 | 30.5969 | 42.6522 | 27.1571 | 40.5414 | 25.3118 | 40.2588 | 23.5657 | 39.9681 | 26.6252 | 83.4773 | 83.3371 | 83.3198 | 60.5362 | 26.6465 | 26.4402 | 97.0104 | 270.8828 | 7.1783 | 100.2708 | 38.34 | 2.81
4 | 30.0518 | 55.1802 | -4.088 | -8.0197 | 4.2677 | 80.8386 | 68.0163 | 32.7223 | 24.2466 | 22.6646 | -6.0505 | 32.8614 | 30.3796 | 28.1265 | 25.602 | 23.7847 | 30.3326 | 44.3497 | 26.6281 | 42.1028 | 24.7053 | 41.7997 | 22.7451 | 41.4513 | 26.6903 | 83.1553 | 83.0137 | 82.9466 | 59.742 | 26.7176 | 26.5065 | 117.9167 | 270.5793 | 7.3137 | 100.4167 | 49.38 | 2.81